## Sheet1
Outdoor Temp (°F) | Humidity (% RH) | Chilled Water Valve Position | System Efficiency Impact (No VFD) | System Efficiency Impact (With VFD) | Primary Penalty Driver
0°F – 50°F | Any | 0% (Closed) | Low Savings (Fan runs 100%) | Max Savings (Fan scales down, valve closed) | Free Cooling: Hydronic valve shuts down entirely. No plant energy used.
55°F – 65°F | Low (<40%) | 10% – 30% | Moderate Penalty (Fan bypasses savings) | High Efficiency (Economizer takes 100% load) | Economizer Window: Air satisfies the space; water valve barely cracks open.
55°F – 65°F | High (>70%) | 60% – 80% | High Flow Penalty | Moderate Penalty | Latent Trap: High dew point forces valve open to wring out moisture.
75°F – 90°F | Moderate (50%) | 70% – 95% | Severe Flow Penalty | Optimized Flow | Sensible + Latent Blend: Valve nears 100% open; max water flow required.
95°F – 110°F | High (>60%) | 100% (Saturated) | Coil Saturation (Low Δ T return) | Managed Saturation (Airflow slows to preserve Δ T) | Low Delta-T Syndrome: Flow peaks, return water stays cold, pumping efficiency collapses.